## Appendix A
Design deliverable check sheets
Appendix A of the deliverable standard
R=U of T requirement; C=Legislative, by-law or code compliance |  | Schematic Design (SD) |  |  | Design Development (DD) |  |  | Construction Document (CD) |  |  | Construction Document (50% CD) |  |  | Construction Document (80% CD) |  |  | Construction Document (100% CD)
No. | Requirement | R | C | Supporting documentation | R | C | Supporting documentation | R | C | Supporting documentation | R | C | Supporting documentation (Submission Package Title) | R | C | Supporting documentation (Submission Package Title) | R | C | Supporting documentation (Submission Package Title) | Notes
General
1 | A Basis of Design (BOD) report documenting design concepts, criteria, project issues and major components including: site, architectural, structural, landscape, mechanical, fire protection, electrical and sustainability. Refer to Appendix B for the requirement of BOD report. | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
2 | Building Information Modelling Execution Plan (BEP) | X | [17 empty] | Initiate in SD but do not update in DD and CD. Could be updated when the CM comes onboard.
3 | BIM model to include key F&S spaces, equipment, and services that includes mechanical, electrical, IT, elevator machine, and main water rooms; roof; ceiling spaces that include serviceable equipment; and service tunnels. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD if required
4 | Clash Detection Report (Identifies major clashes with existing infrastructure) |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
5 | Outline technical specifications following CSI MasterFormat 2020 |  |  |  | X | [14 empty] | Initiate in DD
6 | Technical specifications package following CSI MasterFormat 2020 | [6 empty] | X |  |  | X |  |  | X |  |  | X
7 | Proof of no use or procurement of any equipment is covered under the U.S. National Defense Authorization Act (NDAA), 889(1)(B). | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X
8 | Building system investigation (BSI) if applicable | [18 empty] | The BSI is a standalone non mandatory requirement for the pre-PPR stage.
Accessibility
1 | Preliminary barrier-free compliance report. Confirm that students, faculty and staff spaces conform with accessibility requirements and standards (OBC, AODA IASR and U of T accessibility design standards) | X | [17 empty] | Initiate in SD and complete in SD because this is an initial study
2 | Accessible route plan including exterior and interior barrier-free path of travel, barrier-free entrances, push button locations, ramp slopes, location of barrier-free washrooms with dimensioned clearances (clear space in doors, turning circles, toilet transfer spaces, etc.) |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD if required
3 | Relevant documentation(drawing, specifications, product data sheet) to confirm materials, hardware, fixtures, equipment, furnishings, products, etc. meet accessibility requirements (colour contrast, operation, adaptability). |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
4 | Finalized design drawings, including sections and elevations (windowsill heights, casework configurations, device mounting heights, etc.) |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
Energy modelling
1 | Sustainability Project Charter | X |  |  | X |  |  | X | [8 empty] | X |  |  | Initiate in SD and update in DD and CD
2 | Energy Simulation Files | X |  |  | X |  |  | X | [8 empty] | X |  |  | Initiate in SD and update in DD and CD
3 | Utilities Performance Report | X |  |  | X |  |  | X | [8 empty] | X |  |  | Initiate in SD and update in DD and CD
4 | Scorecard | X |  |  | X |  |  | X | [8 empty] | X |  |  | Initiate in SD and update in DD and CD
5 | Precertification Worksheet | X |  |  | X |  |  | X | [8 empty] | X |  |  | Initiate in SD and update in DD and CD
6 | Water Efficiency Worksheets | X |  |  | X |  |  | X | [8 empty] | X |  |  | Initiate in SD and update in DD and CD
7 | Equipment Cutsheets | X |  |  | X |  |  | X | [8 empty] | X |  |  | Initiate in SD and update in DD and CD
8 | Summary of changes from previous submission |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | Provide summary of changes from SD and DD to current design
9 | Submit metering and verification strategy that outlines which loads are to be metered, types of meters to be specified and calibration certificates. | [6 empty] | X |  |  | X | [5 empty] | X
10 | Life cycle assessment (embodied carbon) | X |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | Initiate in SD and update in DD and CD
11 | Air Leakage Test Report | [18 empty] | Required before Occupancy
Existing conditions
1 | Existing condition assessment including hydronic and air audits | X | [17 empty] | Perform in pre-design
Roofing
1 | Plans and details of vegetative roof system including leak detection, root barrier, drainage layer, growing medium tray system and irrigation system. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Details captured in DD and CD
2 | The type of roof proposed (Lightweight Insulating Concrete, Conventional Modified Bitumen Membrane System, Protected Membrane System) | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Schematic in SD, based details in DD, and full details in CD
Finishes
1 | Floor finishes and reflected ceiling plan, exterior and interior elevations, graphically indicating extent of finishes/materials. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
2 | Data sheet/specification for finishes/materials, listing properties and information including but not limited to physical dimensions, weight, flame-spread rating, thermal resistance, light reflectance values, slip resistance rating, VOC emissions, maintenance/cleaning requirements. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
3 | Material sample board showing finishes used in project (i.e. floor, wall, ceiling, doors, handrails, etc.) |  |  |  | X
Door hardware
1 | Security access plan |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
2 | Barrier free access plan |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD if required
3 | Hardware specifications including closers, door operators, locksets, hinges and exit devices | [6 empty] | X |  |  | X |  |  | X |  |  | X
4 | Door hardware control diagram and sequence of operation | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in CD
Elevators
1 | A traffic analysis to determine number, type and speed of elevators required | X | [17 empty] | Initiate in SD and complete in SD because this is an initial study
2 | Floor plans identifying location of elevators and elevator machine rooms | X |  |  | X | [14 empty] | Initiate in SD and update in DD
3 | Elevator equipment detail (including car controller specifications) | X |  |  | X | [14 empty] | Prepare in DD and CD for U of T's review and formal submission to the regulating authorities
4 | Elevator equipment support details, ensuring proper structural support. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
5 | Description of shaft sump pits, including drainage and pump systems. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
6 | Hoist way plan view, section and elevation for detailed construction layout. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
7 | Elevator entrance assembly plan view, section and elevation |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
8 | Elevator cab interior layouts, including plan view, reflected ceiling plan, front wall elevation, side wall elevation, rear wall elevation,and floor plan specification. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
9 | Elevator signal and fixture drawings, covering Buttons, Indicators and Emergency systems |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
10 | Elevator remote panel(s) drawings for CACF location and other control points. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
11 | Electrical circuit drawings and diagrams for elevator power and control systems. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
12 | Alarm signals and life safety details, including Fire recall systems, Emergency communication systems and Access control systems (e.g., FOBs) |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
13 | TSSA Pre-inspection checklist (20240103) completion, ensuring compliance with safety standards. | [7 empty] | X |  |  | X |  |  | X |  |  | X |  | Initiate in CD
14 | Integration testing documentation confirming proper connection of elevator system to campus security for emergency response. | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in CD
15 | Functional Performance Testing results, including Load testing Speed testing, and Safety system verification (brakes, overspeed governors, door sensors) | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in CD
16 | Commissioning Report, including all test results and verification of system compliance with TSSA, ASME, and applicable codes. | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in CD
17 | As-Built Drawings of final installation, including any deviations from the original design. | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in CD
18 | O&M Manuals from manufacturers, system descriptions, and parts catalog | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in CD
19 | Warranty information | [6 empty] | X |  |  | X |  |  | X |  |  | X
20 | Training Documentation for the University’s F&S team on elevator operations, emergency procedures, and maintenance. | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in CD
21 | Post-Occupancy Review plan, ensuring review of the system's performance 10 months post-acceptance. | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in CD
Fire suppression
1 | Narrative describing the design concept |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
2 | Schematic of each fire protection system |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
3 | Fire protection riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
4 | Connection details to utilities |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
5 | Floor plan identifying the location of fire pump, controller, sprinkler valves, etc |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
6 | Details of specified sprinklers, isolation valves, switches, air dryer, compressors and nitrogen generators | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Complete in CD
7 | Fire department connection and test header location | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in CD
8 | Fire protection zoning plans | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
9 | Floor plans fire protection |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
10 | Location of main headers and risers | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
11 | Fire pump sizing calculation | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
12 | Hydraulic calculations | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
13 | Location of all sprinkler zone valves, drains and fire hose connections | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
14 | Typical detail of sprinkler installation including support detail | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
15 | A complete set of record drawings | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
16 | Fire alarm verification report | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
17 | Fire safety plan copy | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
18 | Floor plans finalized with room numbers | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
19 | Special extinguishing system specifications | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
20 | List of fire extinguisher’s locations | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
21 | Full verification report for fire alarm and sprinkler verification | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
22 | Maglocks design drawings |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Submit in CD
23 | Pressurization fan specifications and installation | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
24 | Kitchen fire suppression system specifications and installation | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
25 | Kitchen exhaust system specifications and installation | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
26 | Fire shutter and fire curtain specifications and installation connected to the fire alarm system | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
27 | Smoke control measures specifications and installation | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
28 | Hold open device installation locations | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
Mechanical
1 | Connection details to the utilities |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
2 | Floor plans ventilation |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
3 | Floor plans heating and cooling piping |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
4 | Floor plans steam and condensate piping |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
5 | Floor plans potable water |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
6 | Floor plans drainage. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
7 | Floor plans laboratory gas piping ie: nitrogen, oxygen, helium, etc. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
8 | Floor plans specialty water piping ie: RO, DI, etc. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
9 | Floor plans fuel oil piping |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
10 | Floor plans natural gas piping |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
11 | HVAC zoning diagrams | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
12 | Floor plans indicating air flow quantities |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
13 | Floor plans indicating pressurization (air flow direction) |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
14 | Floor plans indicating smoke ventilation zones |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
15 | Ventilation system schematics | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
16 | Hydronic heating system schematics | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
17 | Hydronic cooling system schematics | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
18 | Domestic cold water schematics | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
19 | Domestic hot water schematics | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
20 | Sanitary drainage schematics | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
21 | Storm drainage schematics |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
22 | Specialty drainage schematics |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
23 | Specialty water system schematics |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
24 | Steam and condensate system schematics |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
25 | Fuel oil schematics |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
26 | Natural gas schematics |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
27 | Ventilation system riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
28 | Hydronic heating riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
29 | Hydronic cooling riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
30 | Domestic cold water riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
31 | Domestic hot water riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
32 | Specialty water riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
33 | Sanitary drainage riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
34 | Storm drainage riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
35 | Specialty drainage riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
36 | Steam and condensate riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
37 | Specialty gas riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
38 | Fuel oil riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
39 | Natural gas riser diagrams |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
40 | Equipment schedules for major equipment with power and controls information |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
41 | Identifying connection points to existing infrastructure |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
42 | Floor plans identifying main horizontal and vertical service mains | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
43 | Fully dimensioned service shaft layouts. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
44 | Fully dimensioned corridors, service rooms and other critical spaces. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
45 | Major building intakes and exhaust points identified | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
46 | Equipment replacement strategy | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
47 | Mechanical demolition plan | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
48 | Equipment Access per OSHA regulations |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
49 | Drawings and strategy for access and remove major equipment after construction is completed |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
50 | Eddy Current Test | [18 empty] | Required test by a third-party testing company at the factory
51 | Testing, Adjusting, and Balancing (TAB) reports | [18 empty] | Required before Occupancy
52 | TSSA certificate for boilers and pressure vessels (BPVs) | [18 empty] | Required before Ready-for-Takeover
Building automation system (BAS)
1 | BAS Controls network architecture schematic | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
2 | BAS Controls individual system schematics with input and output points |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
3 | BAS dashboard describing energy use and utility consumption of systems |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
4 | BAS sequences of operation |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
Electrical
1 | Connection details to the utilities | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
2 | Load calculations detailing overall project load increase accompanied by submitted Power Request | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
3 | Load calculations detailing equipment/panel loading increases accompanied by submitted Power Request |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Possible to submit for review in DD
4 | Panel schedules detailing existing and new loads in U of T template with associated load numbers |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
5 | Floor plans power |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
6 | Floor plans with panel circuiting |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
7 | Floor plans lighting | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
8 | Floor plans lighting with panel circuiting |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
9 | Single line schematics, making use of provided reference drawing | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
10 | Protection & Controls Narrative | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
11 | Electrical riser drawings |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
12 | LV equipment (three-lines, elevations, single lines), switchgears/switchboard, larger transformer (>112.5kVa), breakers with electronic trip, large ampacity cables/bus ways/bus ducts - metering devices, VFDs | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate for switchgears or switchboard only in SD, for everything else in DD. Update in DD and CD
13 | HV equipment (three-lines, elevations, single line) |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Protection and Control schematics in SD
14 | Electrical room layouts | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
15 | Equipment schedule | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
16 | Identifying connection points to existing infrastructure |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
17 | Major horizontal and vertical services identified |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
18 | Fully dimensioned service shaft layouts. | [6 empty] | X |  |  | X |  |  | X |  |  | X
19 | Equipment replacement strategy | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
20 | Construction phasing strategy and drawings |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
21 | Electrical demolition plan |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
22 | Design standard checkbox review identifying all areas of non-compliance |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Complete in DD and CD, checklist included in the Electrical Design standard
23 | Breaker hoist, tools and accessories |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Complete in DD and CD
24 | Equipment Access per OSHA regulations |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
25 | Drawings and strategy for access and remove major equipment after construction is completed |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
26 | Factory Acceptance Test Requirements | [12 empty] | X |  |  | X |  |  | The FAT must be identified in the project schedule and the Client shall be informed within one month of the planned FAT to ensure that an appropriate Client resource can attend the FAT
26 | Commissioning Test Requirements | [12 empty] | X |  |  | X |  |  | Initiate in CD
Lighting
1 | Lighting conceptual design | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X
2 | Selection of fixture types and lighting control system principles |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
3 | Fixture details, lighting control system specification | [6 empty] | X |  |  | X |  |  | X |  |  | X
4 | Lighting control system architecture | [6 empty] | X |  |  | X |  |  | X |  |  | X
5 | Luminaire, lamp, sensors and controls specification sheets | [6 empty] | X |  |  | X |  |  | X |  |  | X
6 | Lighting calculations for all types of spaces, including foot-candle levels and watts per square foot (lighting power density) and energy density (kWh/gross floor area) based on a specified projected operation. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
7 | A point-to-point photometric layout shall be submitted for each typical space. Layout shall depict average, maximum and minimum illumination values in the horizontal work plane in 30 inches above finished floor level. |  |  |  | X
8 | Additional information may be Required to depict day lighting contribution and the impact to illumination values. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
9 | Reflected ceiling plans, specifications, calculations, renderings and lighting control basis of design |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
Fire alarm
1 | System description | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | To verify system selection from SD to CD
2 | Floor plans fire alarm including panel locations (main fire alarm panel and annunciator panel), duct detectors, door lock, fire/smoke dampers, sprinkler, flow and tamper switches, monitor and control modules, door hold-opens, door lock releases, etc. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
3 | Details of connection to the Central Fire Alarm Monitoring System. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
4 | Details of connections to HVAC, fire pump, fire suppression, door hold-open, etc. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
5 | Zone and active field device descriptions for annunciation and LCD programming | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Review in CD
Landscape
1 | Existing conditions | X
2 | Landscaping concept report | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Update as design progresses
3 | Grading plan (slope) |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
4 | Landscape protection plan |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
5 | Planting plan including type of plant, planting time and ground cover |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
6 | Irrigation plan |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
7 | Protection for existing trees and significant plantings during construction | [6 empty] | X |  |  | X |  |  | X |  |  | X
8 | Soil preparation and planting procedures |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
9 | Bicycle storage location and details | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Update as design progresses (if inside, then not applicable)
10 | Outdoor furniture list and details |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD (campus planning to review)
11 | Soil erosion and sedimentation control |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
12 | Site lighting locations, plans, simulations, specifications, equipment cut sheets and photometrics |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD (utility will look after this)
13 | Stormwater calculations and plan | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Update as design progresses (not reviewed by F&S Grounds Services)
14 | Exterior signage |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD (include building signs only for landscape)
15 | Paving material |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
16 | Skateboard deterrence plan |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
17 | Snow melting system details |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
Site utilities
1 | Utility requirements | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
2 | Site Utilities Plan showing sizes and locations of all Required utility connections. |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
3 | Profiles for underground utilities | [6 empty] | X |  |  | X |  |  | X |  |  | X
4 | Utility connection details | [6 empty] | X |  |  | X |  |  | X |  |  | X |  |  | Require in CD, could initiate in DD
5 | Utility plans, elevations & details for local governing agency approval |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
6 | Sanitary sewer flow calculations |  |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in DD and update in CD
7 | Ground water quality study | x | [17 empty] | Initiate in SD or pre-design
8 | TSSA form: consent to grant third party acces | x |  |  | x |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Once the contract is signed
Security and access control systems
1 | Floor plan indicating all security components (physical access control, intrusion alarm detection systems, video surveillance (CCTV), emergency help stations, panic alarm systems) | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | X |  |  | Initiate in SD and update in DD and CD
2 | As-built drawings showing final design | [18 empty] | This is required at constrution stage.