FIRE SAFETY PLAN

FOR

Click here to enter building name and number

_________________________________________________

Click here to enter address of building

_________________________________________________

PREPARED BY: Click to enter the name of the person preparing this form

_________________________________________________

PREPARED ON: Click to enter a date

_________________________________________________

## Table of contents

Part 1		Introduction									  4

Part 2(a)	Audit of building resources	  5

Part 2(b)	Audit of human resources	10

Part 3		Evacuation procedures for occupants					11

Part 4		Emergency procedures for supervisory staff				12

Part 5		Fire hazards									15

Part 6		Alternative measures for occupant safety				             16

Part 7		Fire drills									17

Part 8		Requirements of the Ontario Fire Code					18

Part 9		Delegation of responsibilities and maintenance requirements	             19

Fire Department access							19

Closures and means of egress						19

Portable fire extinguishers						             20

Exit lighting and emergency lighting systems			             20

Fire alarm systems							             22

Smoke alarms								24

Interconnected smoke alarms						25

Carbon monoxide alarms						             26

Sprinkler systems								27

Standpipe and hose systems						30

Fire pumps									33

Private hydrants								34

Commercial cooking equipment					             36

Fixed extinguishing systems						37

Elevators									37

Emergency power systems						             39

Smoke control measures						             40

Smoke shafts and venting equipment					40

Service equipment								42

Water supplies for fire protection (water tanks)			             43

Part 10	Additional information							46

Part 11	Building schematics							             47

Part 12	Site plan									48

Persons requiring assistance form					             49

## Part 1		Introduction

As per the Ontario Fire Code sentence 2.8.2.1.(4), “The fire safety plan shall be reviewed as often as necessary, but at least every 12 months, and shall be revised as necessary so that it takes into account changes in the use or other characteristics of the building or premises.”

It is the responsibility of the owner (defined by the Ontario Fire Code as any person, firm or corporation controlling the property under consideration) to ensure that the information contained within the Fire Safety Plan is accurate and complete.

The Fire Protection and Prevention Act, Part VII, Section 28, outlines that in the case of an offence for contravention of the fire code, a corporation is liable to a fine of not more than $500,000 for a first offence and not more than $1,500,000 for a subsequence offence. An individual is liable to a fine of $50,000 for a first offence and not more than $100,000 for a subsequent offence or imprisonment for a term of not more than one year or both.

The Ontario Fire Code and the Fire Protection and Prevention Act 1997 can be viewed online via the following link: https://www.ontario.ca/laws/regulation/070213.

Additionally, the Ontario Fire Code sentence 2.8.2.1.(3) of Division B states, “the fire safety plan shall be kept in the building or on premises in an approved location.”

Under the Toronto Municipal Code Chapter 470, Fire safety boxes, all buildings that are required to prepare a Fire Safety Plan under section 2.8 of the Ontario Fire Code must install a fire safety box, or a fire safety box and lock box. Ensure the installed fire safety plan box location adheres to this by-law.

The location of the Fire Safety Plan box is:

Please enter the location of the Fire Safety Plan box

_________________________________________

## Part 2(a)		Audit of building resources

Occupancy type					Select Your Occupancy Type

Access

Designated fire route	Do you have a designated fire route?

Nearest municipal hydrant	Type in a brief description of the location.

Private hydrants					Do you have private hydrants on site?

Fire alarm system					Do you have a fire alarm system?

Fire alarm type					If yes, what type of system do you have?

Is your fire alarm zoned				Please select a response.

Make	Enter the Make of the Fire Alarm System.

Model	Enter the Model of the Fire Alarm System.

Location of fire alarm panel			Enter the location of the Fire Alarm panel.

Location of fire alarm annunciator panel	Enter the location of the Fire Alarm annunciator panel.

Heating	Natural gas ☐  Electric ☐ 			Other:

Main gas shutoff	No  ☐   Yes ☐

Location:

Enter the location of main electrical shutoff

Main electrical shutoff location

Enter location of main domestic water shutoff

Main domestic water shutoff location

If you have magnetic locks or door 			Please select a response.
release devices, are they activated by
the fire alarm system?

Sprinkler system					Do you have a sprinkler system?

If yes, is it connected to the fire 	Please choose a response.
	alarm system?

The system is:					Wet   ☐			Dry   ☐

Antifreeze loop  ☐		Deluge  ☐

Foam   ☐			Preaction  ☐

Mist  ☐

Other_________________________

Standpipe system					Do you have a standpipe system?

If yes, the system is:	Wet   ☐	Dry   ☐

Fire department connection	Do you have a Fire Department connection?

If yes, briefly indicate where it is located.

Fire pump						Do you have a fire pump?

If yes, what model					Please indicate the model.

Fixed extinguishing system for commercial cooking

Do you have a fixed system?	Please choose a response.

If you have a fixed extinguishing system, what type?

Please select which type of system you have.

Is your system connected to the			Please choose a response.
	fire alarm system?

Is there an audible bell? 	Please choose a response.

Is there a visual indicator?	Please choose a response.

Fuel source of cooking equipment	Natural gas   ☐	 Electric   ☐

Solid fuel   ☐

Fixed extinguishing system for spray booth		Do you have a fixed system?

If yes, what type?	Please select which type of system you have.

Is your system connected to the	Please choose a response.                
	fire alarm system?

Is there an audible bell? 	Please choose a response.

Is there a visual indicator?	Please choose a response.

Other fixed extinguishing systems

Please list any other extinguishing systems you might have, (that is, pre-action, sprinkler, halon, inergen, dry chemical).

Please click here to enter your other extinguishing systems present

Emergency power

Do you have emergency back-up power?	Please choose a response.

If yes, please indicate which form?	Please choose an item.

What is connected to your emergency power?

Click or tap here to enter what equipment will operate from the use of your emergency power.

Generator

If you have a generator, how is it fuelled?	Please choose an item.

If other, please list how it is fuelled:	Click or tap here to enter text.

Please list the equipment that is powered by the generator:

Please click or tap here to enter your equipment powered by your generator.

Hazardous areas

Do you have any hazardous areas on premise that should be identified?

Please choose a response.

If yes, please identify.

Please click or tap here to enter your hazardous areas.

Spill control measures

Does your location require spill control measures?	Please choose a response.

Where are your SDS sheets located?

Click or tap here to enter a brief description of where your SDS sheets are located.

If you require spill control measures, add procedures in Part 10 – Additional Information.

Elevators

Do you have elevators on premise?	Please choose a response.

If yes, please select which designation you have:

☐	Firefighter elevator (Red Helmet Designation)

☐	Firefighter service (Yellow Helmet Designation)

☐	No designation

Location of recall/operating keys:

Please click or tap here to enter the location of recall/operating keys.

If there are any special operating instructions (that is, how they recall in a state of alarm), please outline below.

Please click or tap here to enter special operating instructions.

Provide procedures for the use of elevators in the event of a fire.

Click or tap here to enter procedures for the use of elevators in the event of a fire.

## Part 2(b)		Audit of human resources

Building owners:			The Governing Council of the University of Toronto

27 King’s College Circle, Toronto, ON, M5S 1A1

416-427-4963

After hours contacts (24-hour telephone numbers)

Campus Safety    416-978-2323

Building operator:			Click to enter building operator name

Monitoring company			Click to enter name of fire alarm monitoring company

Click to enter phone number of fire alarm monitoring company

Other important contacts	Click to enter any other important contacts, with phone number

## Part 3		Evacuation procedures for occupants

Emergency procedure signage will be affixed to the wall at all fire alarm pull station (when fire alarm system is not monitored) or one per floor area where the building is monitored, as per Division B, Article 2.8.2.5. of the Ontario Fire Code

The following are examples of emergency procedure signs that can be posted for occupants to follow.

If you require assistance and cannot evacuate or have retuned because of fire or heavy smoke, shelter in place.

- Close the door but leave it unlocked for possible entry by fire fighters.

- Call Campus Safety 416-978-2222 or 911 and tell them where you are.

- Keep smoke from entering your suite, place clothing or wet towels at the bottom of the door and seal vents or air ducts the same way.

- Keep low to the floor if smoke enters the suite.

- Wait to be rescued. Remain calm. Do not panic.

## Part 4		Emergency procedures for supervisory staff

The following is a list of positions who are considered supervisory staff

Click to enter a list of positions considered supervisory staff

As per the Ontario Fire Code, supervisory staff shall be instructed in the fire emergency procedures as described in the fire safety plan before they are given any responsibility for fire safety.

How are the supervisory staff trained?

Click here to outline training education for performing supervisory staff

Duties of supervisory staff

Click here to enter the duties that supervisory staff are responsible for

Do you have any occupants who require assistance evacuating in an emergency?

Please Choose an item

If yes, please complete the form, “persons requiring assistance” at the end of this document and keep it with your Fire Safety Plan.

Supervisory staff will be trained on voice communication systems and smoke control procedures in high buildings.

Complete this section ONLY if your building is greater than 6 storeys.

Suggested operation of portable fire extinguishers

In the event of a fire, the ability to either control or confine the fire will greatly impact fire service operations.

NEVER FIGHT A FIRE:

- If the fire could block your only exit

- If the fire is spreading quickly

- If the fire is too large

- If the type or size of the extinguisher is wrong

- If you don’t know how to use a fire extinguisher

If you become aware of a small fire and believe that it may be extinguished using a portable fire extinguisher, follow the P.A.S.S. acronym.

The graphic is of a portable fire extinguisher with the acronym PASS, P is for pull the pin, A is for aim the hose at the base of the fire, S is for squeeze the lever and S is for sweep from side to side.

Special notes:

- Keep extinguishers in a visible area without obstructions around them.

- Never rehang extinguishers after use.

- After use, ensure the extinguisher is properly recharged by a person that is qualified to service portable fire extinguishers, ensure a replacement extinguisher is provided.

- Prior to using a K-type extinguisher (commercial kitchens), activate the kitchen extinguishing system to avoid electrocution and shut off fuel sources (gas/electrical) if it is safe to do so.

Use of a portable fire extinguisher is strictly a voluntary act.

## Part 5		Fire hazards

Residential properties

To avoid fire hazards in the building, occupants must:

- Always clean out the clothes dryer lint collector before and after use.

- Avoid careless smoking and use designated smoking areas. Never smoke in bed.

- Avoid unsafe cooking practices; deep fat frying, cooking with excessive heat, unattended stoves and loosely hanging sleeves.

- Do not use unsafe electrical appliances, frayed extension cords, overloaded outlets or temporary wiring for permanent use.

- Never dispose of flammable liquids or aerosol cans in garbage chutes.

- Never force cartons, coat hangers, bundles of paper or any oversized item into the chute, as it may become blocked.

- Never leave anything that may burn or cause a trip hazard in the halls, corridors and/or stairways.

- Never put burning material such as cigarettes and ashes into the garbage chute.

Commercial, retail and industrial properties

A high standard of housekeeping and building maintenance is an important factor in the prevention of a fire. Please ensure the following:

- Combustible materials are stored only in approved areas.

- Dispose of oily rags in proper containers.

- Do not use defective electrical wiring and/or appliances; avoid over-fusing, and the use of extension cords as permanent wiring.

- Ensure that the clothes dryer lint collector is cleaned out after each use and is properly vented.

- Ensure fire and smoke barrier doors are operating properly and never wedged open.

- Only smoke in designated smoking areas and avoid careless smoking.

- Properly clean kitchen hoods and filters.

- Properly store flammable liquids and gases

## Part 6		Alternative measures for occupant safety

Procedures to be followed in the event of shutdown, or any part of a fire protection system out of service, are listed below. Also, in the event of any shut-down of fire protection equipment systems or part thereof, in excess of 24 hours, the Fire Department shall be notified in writing/email. Occupants shall be notified and instructions posted as to alternative provisions or actions to be taken in case of emergency. These provisions and actions must be acceptable to the Chief Fire Official.

All attempts to minimize the impact of malfunctioning equipment will be initiated. Where portions of a sprinkler or fire alarm system are placed out-of-service, service to the remaining portions must be maintained. Where necessary, a fire watch will be initiated to patrol the building and notify occupants of a fire emergency.

Notify the Toronto Fire Service Communications Division, dial 416-338-9000 (do not use 911).

Give:

ü Your name	ü A description of the problem

ü Address of the shutdown	ü When you expect the shutdown to be corrected

ü A direct contact phone number

- Post notices on all floors by elevators and in the lobby entrance, stating the problem and when it is expected to be corrected.

- Have staff or other reliable person(s) patrol the affected area(s) at least once every hour and document their Fire Watch patrols.

- Notify Toronto Fire Services and the building occupants when repairs have been completed and systems are operational.

Note: In commercial kitchens, cooking operations shall be suspended until the commercial cooking fixed extinguishing system is restored.

## Part 7		Fire drills

Fire drills shall be conducted in compliance with the Ontario Fire Code requirements and the fire drill procedures shall be prepared in consultation with the Chief Fire Official.

All fire drill logs will be retained on site for a period of at least 12 months after the drills. Fire drill logs will identify the date and type of drill, persons participating, fire drill scenario, and the summary analysis and outcomes of the fire drill.

Fire drills for your business/property type are required to be conducted every:

Please make a selection.

The Ontario Fire Code (2.8.3.1.(1) of Div. B) states that the procedure for conducting fire drills shall be included in the fire safety plan, taking into consideration:

- The building occupancy and its fire hazards.

- The safety features provided in the feature.

- The desirable degree of participation of occupants other than supervisory staff.

- The number and degree of experience of participating supervisory staff.

- The testing and operation of emergency systems installed in buildings within the scope of Subsection 3.2.6 of Division B of the Ontario Building Code.

Note: In hotels, every employee shall participate in at least one fire drill within a 12-month period.

If the fire alarm is monitored by central monitoring, Campus Safety shall be notified before and after each fire drill at 416-978-2323.

or

If the fire alarm is monitored by a third-party monitoring company, Toronto Fire Services shall be notified before and after each fire drill. Contact the Communications Division at 416-338-9000.

## Part 8		Requirements of the Ontario Fire Code

Check / inspect / test requirements of the Ontario Fire Code

To assist you in fulfilling your obligations, included is a list of portions of the Ontario Fire Code that requires checks, inspections and/or tests to be conducted for the facilities. It is required that you read over this list and perform or have performed the necessary checks, inspections and/or tests for the items that apply to your property.

Fire prevention officers may check to ensure that the necessary checks, inspections and/or tests are being done, when conducting their inspections.

This list has been prepared for purposes of convenience only. For accurate reference, the Ontario Fire Code should be consulted.

Definitions for key words are as follows

Check			Means visual observation to ensure the device or system in in place.

Inspect	Means physical examination to determine that the device or system will apparently perform in accordance with its intended function.

Test	Means the operation of a device or system to ensure that it will perform in accordance with its intended operation or function.

1.1.2.2.(1) of the Ontario Fire Code states, “Subject to Sentence (2), the original or a copy of any record required by this Code shall be retained at the building to which the record relates:

- for a period of at least two years after being prepared.

- so that at least the most recent and the immediately preceding record of a given test or inspection are retained.

## Part 9	Delegation of responsibilities and maintenance requirements

Fire Department access

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Check | 2.5.1.3 | Fire access routes shall be maintained to be immediately ready for use at all times by fire department vehicles. | As required | Please select a designate. |

Closures and means of egress

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Check | 2.2.3.2.(1) | Closures in fire separations shall be maintained to ensure that they are always operable. | As required | Please select a designate. |
| Check | 2.2.3.4.(2) | Doors in fire separations shall be checked as frequently as necessary to ensure they remain closed. | As required | Please select a designate. |
| Inspect | 2.2.3.4.(4) | A door in a fire separation shall be inspected monthly. | Monthly | Please select a designate. |
| Check | 2.7.1.7 | Means of egress shall be maintained in good repair and free of obstructions. | As required | Please select a designate. |
| Inspect | 2.2.3.5 | Fire dampers and fire-stop flaps shall be inspected annually, or an approved time schedule. | Annually | Please select a designate. |

Portable fire extinguishers

*Additional reference NFPA 10

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Inspect | 6.2.7.2 | Portable extinguishers shall be inspected. | Monthly | Please select a designate. |
| Inspect | 6.2.7.1.(1) | Maintenance and testing of portable extinguishers shall be in conformance with NFPA 10, “Portable Fire Extinguishers. | Annually | Contractor |
| Test | 6.2.7.1.(1) | Hydrostatically test carbon dioxide and water extinguishers. | Every 5 years | Contractor |
| Test | 6.2.7.1.(1) | Hydrostatically test dry chemical and vaporizing liquid type extinguishers. | Every 12 years | Contractor |

Exit lighting and emergency lighting systems

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Check | 2.7.3.1 | Maintain all exits signs to ensure that they are clean, visible and legible. | As required | Please select a designate. |
| Check | 2.7.3.2 | Exit signs shall be illuminated externally or internally, as appropriate for the sign’s design, while the building is occupied. | As required | Please select a designate. |
| Check | 2.7.3.3.(1) | Pilot lights on emergency lighting unit equipment shall be checked monthly for operation. | Monthly | Please select a designate. |
| Inspect | 2.7.3.3.(2) | Batteries shall be inspected and maintained as per manufacturers specifications. (Ensuring battery: i) Surface is clean and dry, ii) Terminal connections are clean, iii) Free of corrosion and lubricated, iv) terminal clamps are clean and tight. | Monthly | Please select a designate. |
| Test | 2.7.3.3.(3)(a) | Emergency lighting unit equipment shall be tested to ensure that the emergency lights will function upon failure of the primary power supply. | Monthly | Please select a designate. |
| Test | 2.7.3.3.(3)(b) | Emergency light unit equipment shall be tested to ensure that the unit will provide emergency lighting for a duration equal to the design criteria under simulated power failure conditions. | Annually | Please select a designate. |
| Test | 2.7.3.3.(4) | The charging conditions for voltage and current and the recovery period will be tested to ensure that the charging system is in accordance with the manufacturer’s specifications. | Annually | Please select a designate. |

Fire alarm system

*Additional reference to CAN/ULC-S536		 ☐ Check if this section is not applicable

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Check | 6.3.1.1. | Check to ensure access to the fire alarm and voice communication system components are unobstructed. | Daily | Please select a designate. |
| Check | 6.3.2.3. | The central alarm and control facility shall be checked for indication of trouble in the system. | Daily | Please select a designate. |
| Inspectand test | 6.3.2.2.(1) | Except as provided in sentence (2), a fire alarm system, with or without voice communication capability shall be inspected and tested in conformance with CAN/ULC-S536, “Inspection and Testing of Fire Alarm Systems.” |  |  |
| Test | 6.3.2.2.(1) CAN-ULC-S536-04 Article 4 | Test all fire alarm system components while on emergency power supply. | Monthly | Please select a designate. |
| Inspect andtest | 6.3.2.2.(1) CAN-ULC-S536-04 Article 5 | Inspect and test all fire alarm system components by persons certified for service of fire alarm services. | Annually | Contractor |
|  | 6.3.2.2.(4) | A record of each device, component and circuit of the fire alarm system that is inspected and tested in accordance with Sentence (1) shall (a) indicate whether the device, component or circuit is in proper working order, and (b) be kept in accordance with subsection 1.1.2. | Monthly and annually | Please select a designate. Contractor |
| Test | 6.3.2.4. | Voice communication systems that are integrated with a fire alarm system shall be tested in conformance with CAN/ULC-S536, “Inspection and Testing of Fire Alarm Systems.” | Annually | Contractor |
| Test | 6.3.2.5.(1) | Test voice communication systems that are not integrated with a fire alarm system. | Monthly | Please select a designate. |
| Test | 6.3.2.5.(2) | Loudspeakers shall be tested monthly as an all-call signal to ensure they function as intended. | Monthly | Please select a designate. |
| Test | 6.3.2.5.(3) | Communication from at least one remote firefighter emergency telephone location to the control unit shall be tested on a rotational basis. All remote firefighter emergency telephone locations are to be tested at least once per year. | Monthly | Please select a designate. |

Smoke alarms					☐ Check if this section is not applicable

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
|  | 6.3.3.4. | The landlord of each rental suite shall give the tenant a copy of the smoke alarm manufacturer’s maintenance instructions or approved alternative maintenance instructions. | As required | Manager |
| Test | 6.3.3.8.(2) | Test smoke alarm annually and after every change in tenancy. | Annually | Please select a designate. |
| Test | 6.3.3.8.(3) | Test battery-operated smoke alarms after the battery is replaced. | As required | Please select a designate. |
| Inspect | 6.3.3.3.(1) | Maintain smoke alarms. (For example, ensuring cleaning of alarm and smoke chamber, proper installation, installation of fresh batteries and testing of alarm function.) | Annually | Please select a designate. |
|  | 6.3.3.7.(1) | A smoke alarm shall be replaced within the time frame indicated in the manufacturer’s instructions. | As required | Please select a designate. |
| Check | 2.13.2.1.(1)(a)(b) | Check smoke alarms installed between each sleeping area in the hallway and/or remainder of the dwelling unit. | Annually | Please select a designate. |
| Check | 2.13.2.1.(1)(d) | Ensure that smoke alarms are installed on each storey of a dwelling unit without a sleeping area. | Annually | Please select a designate. |

Interconnected smoke alarms

*Additional reference CAN/ULC S552		☐ Check if this section is not applicable

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Check | 6.3.2.6.(3) | The power supply shall be checked. | Weekly | Please select a designate. |
| Test | 6.3.2.6.(4) | Test at least one smoke alarm using its test function, on a rotational basis. | Monthly | Please select a designate. |
| Test | 6.3.2.6.(5) | Test every pull station to ensure a complete activation. | Annually | Please select a designate. |
|  | 6.3.2.6.(6) | Written records shall be kept of weekly checks of the power supply for at least six months after they are made and be available upon request to the Chief Fire Official. | Weekly | Please select a designate. |

The above is not applicable to single family homes or two-unit residential occupancies as per 6.3.2.6.(1)

Carbon monoxide alarms				☐ Check if this section is not applicable

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Inspect | 6.3.4.3.(1) | Carbon monoxide alarms shall be maintained in operating condition. (For example, ensuring cleaning of alarm, properly installed, installation of fresh batteries and testing of alarm function.) | Annually | Please select a designate. |
|  | 6.3.4.4. | The landlord of each rental suite of residential occupancy shall give the tenant a copy of the carbon monoxide alarm manufacturer’s maintenance instructions or approved alternative maintenance instructions. | As required | Manager |
|  | 6.3.4.7.(3) | A carbon monoxide alarm shall be replaced within the time frame indicated in the manufacturer’s instructions. | As required | Please select a designate. |
| Test | 6.3.4.8.(2) | Carbon monoxide alarms shall be tested annually and after every change in tenancy. | Annually / As required | Please select a designate. |
| Test | 6.3.4.8.(3) | The landlord shall test battery-operated carbon monoxide alarms after the battery is replaced. | Annually / As required | Please select a designate. |

Sprinkler systems					☐ Check if this section is not applicable

*Repairs / replacement / alterations – Reference NFPA 13

Inspection / testing / maintenance – Reference NFPA 25

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Inspect | 6.5.4.1. | Auxiliary drains shall be inspected to prevent freezing. | As required | Please select a designate. |
| Check | 6.5.4.5.(1) | Unsupervised valves controlling sprinkler water supplies or alarms shall be sealed in the open position. | Weekly | Please select a designate. |
| Inspect | 6.5.4.5.(2) | Electronically supervised valves or valves that are locked open shall be inspected. | Monthly | Please select a designate. |
| Check | 6.5.3.2. | Water supply pressure and system air or water pressure shall be checked by using gauges to ensure that the system is maintained at the required operating pressure. | Weekly | Please select a designate. |
| Test | 6.5.5.2.(1) | On all unsupervised sprinkler systems, test sprinkler alarms using the alarm test connection located at the sprinkler valve. | Monthly | Please select a designate. |
| Test | 6.5.5.7.(2) | If electrical supervision is provided for a sprinkler system, transmitters and water-flow-actuated devices shall be tested. | Every 2 months | Please select a designate. |
| Test | 6.5.5.7.(3) | If electrical supervision is provided for a sprinkler system, valve supervisory switches, tank water level devices, building and tank water temperature supervisory devices and other sprinkler system supervisory devices shall be tested. | Every 6 Months | Contractor |
| Check | 6.5.3.1. | Exposed sprinkler piping hangers shall be checked to ensure that they are kept in good repair. | Annually | Contractor |
| Check | 6.5.3.4. | Sprinkler heads shall be checked to ensure that they are free from damage, corrosion, grease, dust, paint or whitewash. | Annually | Contractor |
| Test | 6.5.5.3. | On wet sprinkler systems, water-flow alarm test using the most hydraulically remote test connection shall be performed. | Annually | Contractor |
| Test | 6.5.5.5. 6.5.5.6. | Sprinkler system water pressure shall be tested annually or after any sprinkler system control valve has been operated, with the main drain valve fully open, to ensure that there are no obstructions or deterioration of the main water supply. | Annually | Contractor |
| Inspect | 6.5.4.4.(2) | Plugs or caps on Fire Department connections shall be removed annually and the threads inspected for wear, rust or obstruction and corrective action shall be taken as needed. Re-secure plugs or caps, wrench tight. | Annually | Contractor |
| Check | 6.5.3.3. | Dry-pipe valve rooms or enclosures in unheated buildings shall be checked as often as necessary when the outside temperature falls below 0o Celsius to ensure that the system does not freeze. | As required | Please select a designate. |
| Inspect | 6.5.4.3. | The priming water supply for dry-pipe systems shall be inspected to ensure that the proper level above the dry pipe valve is maintained. | Every 3 months | Please select a designate. |
| Test | 6.5.5.4. | Dry-pipe valves shall be trip tested annually. A full flow trip test, with the control valve fully open, shall be conducted at least every 3 years. | Annually | Contractor |
| Inspect | 6.5.4.2. | Dry-pipe systems shall be inspected for obstructions in the sprinkler piping and, if necessary, the entire system flushed of foreign material. | Every 15 years | Contractor |

Standpipe and hose systems			☐ Check if this section is not applicable

*Additional reference to NFPA 25

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Inspect | 6.4.2.1. | Hose stations shall be inspected to ensure that the hose is in proper position and that all the equipment is in place and in operable condition. | Monthly | Please select a designate. |
| Inspect | 6.4.2.4. | Hose valves shall be inspected to ensure that they are tight so that there is no water leakage into the hose. | Annually | Contractor |
| Inspect | 6.4.2.5. | Standpipe hose shall be unracked, unreeled or unrolled and inspected annually and after use, and any worn hose or gaskets in the couplings at the hose valves and at the nozzle replaced. If the hose is replaced on the rack, reel or storage area, it shall be re-racked, re-reeled or re-rolled so that any folds do not occur at the same position they were previously on the hose. | Annually | Contractor |
| Inspect | 6.5.4.4.(2) | Plugs or caps on Fire Department connections shall be removed annually and the threads inspected for wear, rust or obstruction and corrective action shall be taken as needed. Re-secure plugs or caps, wrench tight. | Annually | Contractor |
| Test | 6.4.3.6. | Standpipe system piping which normally remains dry shall be hydrostatically tested at intervals not greater than 5 years per OFC. | Every 5 years | Contractor |
| Test | 6.4.3.1.(1) | Standpipe systems that have been modified, extended or are being restored to service after a period of disuse exceeding one year shall be tested. | As required | Contractor |
| Test | 6.4.3.7.(1) | The dry portion of the fire department connection piping of a standpipe system shall be hydrostatically tested at a pressure of not less than 1050 kPa (gauge) for 2 hours where: - the fire department connection piping has been in service for more than thirty years, or the age of the fire department connection piping cannot be determined. | Every 5 years | Contractor |
| Inspect | 6.4.3.7.(3) | Fire department connection piping shall be inspected annually with any plugs or caps removed to ensure that: - the fire department connection is physically unobstructed and readily accessible, - the fire department connection identification sign is in place and visible, - the fire department connection is free of wear, rust or obstruction, - couplings or swivels are not damaged and rotate smoothly, - gaskets are in place and in good condition, - the check valve is not leaking, - the automatic drain valve is in place and operating properly, and fire department connection clappers are in place and operating properly. | Annually | Contractor |

Fire pumps						☐ Check if this section is not applicable

*Additional references to NFPA 25

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Check | 6.6.3.1. | The water level in the fire pump reservoir. | Weekly | Please select a designate. |
| Check | 6.6.3.2. | The temperature of pump rooms shall be checked during freezing weather. | Daily | Please select a designate. |
| Test | 6.6.3.3.(1) | Fire pumps shall be operated at rated speed. | Weekly | Please select a designate. |
| Inspect | 6.6.3.3.(2) | Fire pump discharge pressure, suction pressure, lubricating oil level, operative condition of relief valves, priming water level and general operating conditions. | Weekly | Please select a designate. |
| Test | 6.6.3.4.(1) | Internal combustion engine fire pumps shall be operated for a sufficient time to bring the engine up to normal operating temperature. | Weekly | Please select a designate. |
| Inspect | 6.6.3.4.(2) | The storage batteries, lubrication systems, oil and fuel supplies. | Weekly | Please select a designate. |
| Test | 6.6.3.5. | Fire pumps shall be tested at full rated capacity to ensure that they can deliver the rated flow. | Annually | Contractor |

Private hydrants					☐ Check if this section is not applicable

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Check | 6.6.4.3. | Hydrants shall be inspected annually and after each use. | As required | Please select a designate. |
| Inspect | 6.6.5.1. | Hydrants shall be inspected annually and after each use. | Annually | U of T Fire Prevention |
| Inspect | 6.6.5.2.(1) | Hydrants shall be equipped with port caps that are secured wrench tight. | Annually | U of T Fire Prevention |
| Inspect | 6.6.5.2.(2) | Port caps shall be removed and the connections inspected for wear, rust or obstructions that in any way hamper easy removal and corrective action shall be taken as needed. | Annually | U of T Fire Prevention |
|  | 6.6.5.2.(3) | If the caps are missing, the hydrant shall be examined for obstructions or accumulated refuse and flushed and the port caps shall be re-installed. | As required | U of T Fire Prevention |
| Inspect | 6.6.5.3. | The hydrant barrel shall be inspected to ensure that no water has accumulated within the barrel when the main valve is in the closed position. | Annually | U of T Fire Prevention |
| Inspect | 6.6.5.4. | Where the hydrant barrel is found to contain water under Article 6.6.5.3., the drain valve shall be inspected for operation. | Annually | U of T Fire Prevention |
| Inspect | 6.6.5.6. | Hydrant water flow shall be inspected. | Annually | U of T Fire Prevention |
| Check | 6.6.5.7. | The main valve of the hydrant shall be fully opened, and the hydrant operated with one port open, and the water flow checked. | Annually | U of T Fire Prevention |

Commercial cooking equipment			☐ Check if this section is not applicable

*Additional references to NFPA 96

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
|  | 2.6.1.13. | Exhaust and fire protection systems required under Article 2.6.1.12. shall be maintained in accordance with NFPA 96, “Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations.” |  | Please select a designate. |
|  | 6.2.6.12. | Portable extinguishers suitable for Class K fires shall be provided to protect cooking operations. |  | Please select a designate. |
| Check | 2.6.1.3.(1) | Hoods, ducts and filters subject to accumulations of combustible deposits shall be checked and shall be cleaned if the accumulation of combustible deposits creates a fire hazard. | At intervals not greater than 7 days | Please select a designate. |
| Inspect | 6.8.2.1.(1) | Except as otherwise provided in this Section, where special fire suppression systems have been installed, inspection and maintenance shall be provided in conformance with the appropriate standards set out in Sentences 6.8.1.1. (3), (4) and (5). | As often as required but no less than every 6 months | Please select a designate. |
| Inspect | 2.6.1.13 NFPA 96 11.4 | The entire exhaust system shall be inspected for grease buildup and cleaned by a properly trained, qualified and certified person. | Select your frequency | Contractor |

Fixed extinguishing systems			 ☐ Check if this section is not applicable

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Inspect | 6.8.2.1.(1) | Except as otherwise provided in this Section, where special fire suppression systems have been installed, inspection and maintenance shall be provided in conformance with the appropriate standards set out in Sentences 6.8.1.1. (3), (4) and (5). | As often as required but no less than every 6 months | Please select a designate. |

Elevators						☐ Check if this section is not applicable

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
|  | 7.2.5.1.(2) | The keys required to recall elevators and to permit independent operation of each elevator shall be kept in an approved location. |  | Please select a designate. |
|  | 7.2.5.1.(4) | The firefighters’ elevator symbol shall be maintained in identifiable condition. |  | Please select a designate. |
| Test | 7.2.2.1.(1) | Elevator door opening devices operated by means of photo-electric cells shall be tested to ensure that the devices become inoperative after the door has been held open for more than 20 seconds with the photo-electric cell covered. | Every 3 months | Please select a designate. |
| Test | 7.2.2.1.(2) | Key-operated switches located outside an elevator shaft shall be tested to ensure that actuation of the switch will render the emergency stop switch in each car inoperative and bring all cars to the street floor or transfer lobby by cancelling all other calls after the car has stopped at the next floor at which it can make a normal stop. | Every 3 months | Please select a designate. |
| Test | 7.2.2.1.(3) | Key-operated switches in each elevator car shall be tested to ensure that actuation of the switch will: (a) enable the elevator to operate independently of other elevators, (b) allow operation of the elevator without interference from floor call buttons, (c) render door protective devices inoperative, and (d) control the opening of power-operated doors only by continuous pressure on the door-opening buttons or switches, to ensure that if the “OPEN” button or switch is released while the door is opening, the doors will automatically close. | Every 3 months | Please select a designate. |

Emergency power systems				☐ Check if this section is not applicable
*Additional reference to CSA C282, “Emergency Electrical Power Supply for Buildings”

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Inspect & Test | 6.7.1.1. | Except as provided in Sentence (2), and Articles 6.7.1.2. to 6.7.1.5., emergency power systems shall be inspected, tested and maintained in conformance with CSA-C282, “Emergency Electrical Power Supply for Buildings.” | Weekly Monthly Every 6 months Annually Every 5 years | Please select a designate. Please select a designate. Please select a designate. Please select a designate. Please select a designate. |
|  | 6.7.1.3. CSA-282 Article 11.1.2 | A permanent log of the inspection, testing and maintenance of the emergency power supply system shall be maintained in accordance with the manufacturer’s manual of operating and maintenance instructions and cover the items inspected and tested weekly, monthly, every six months, annually and every five years. | As required | Please select a designate. |
|  | 6.7.1.5. | Liquid fuel storage tanks shall be drained and refilled with fresh fuel at intervals not greater than 12 months. | Annually | Please select a designate. |

Smoke control measures				☐ Check if this section is not applicable

| Check, inspect or test | Ontario Fire Code reference | Action | Responsibility |
| --- | --- | --- | --- |
| Inspect and test | 7.3.1.2. | Where smoke control measures contained in Commentary C of NRC, User’s Guide –NBC 1995, “Fire Protection, Occupant Safety and Accessibility (Part 3)” are used, the inspections and tests shall be carried out as outlined in Section 7.3 of Division B of NRC, “National Fire Code of Canada.” | Please select a designate. |
| Inspect and test | 7.3.1.3.(1) | Subject to Sentences (2) to (5), where a smoke control system is designed to meet the requirements of the Building Code, the inspections and tests for equipment shall be carried out in accordance with procedures established by the designer of the system. | Please select a designate. |

Smoke shafts and venting equipment		☐Check if this section is not applicable

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Inspect | 7.2.3.1.(1) | Closures in vent openings into smoke shafts from each floor shall be inspected sequentially over a period not to exceed five years. | Every 5 years | Contractor |
| Inspect | 7.2.3.1.(2) | Every closure in an opening to the outdoors at the top of a smoke shaft, shall be inspected to ensure that it will open: a) manually from outside the building b) on a signal from the smoke or heat actuated device in the smoke shaft, and c)when a closure in an opening between a floor area and the smoke shaft opens. | Annually | Contractor |
| Inspect | 7.2.3.1.(3) | All elevators in an elevator shaft, that is intended for use as a smoke shaft, shall be inspected to ensure that on activation of the fire alarm system, the elevators will return to the street floor and remain inoperative. | Every 6 months | Please select a designate. |
| Inspect | 7.2.3.1.(4) | Where an air-handling system is used for venting floor areas in the event of a fire to comply with the requirements of the Building Code, the system shall be inspected to ensure that air is exhausted to the outdoors. | Annually | Contractor |
|  | 7.2.5.1.(5) | Access to windows and panels required to vent floor areas and vents to vestibules that are permitted to be manually openable shall be kept free of obstructions. | As required | Please select a designate. |

Service equipment					☐ Check if this section is not applicable

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
| Inspect | 2.2.3.5. | Fire dampers and fire-stop flaps shall be inspected annually, or an approved time schedule. | Annually | Please select a designate. |
| Check | 2.6.1.3.(1) | Hoods, ducts and filters subject to accumulations of combustible deposits shall be checked and shall be cleaned if the accumulation of combustible deposits creates a fire hazard. | Weekly | Please select a designate. |
| Inspect | 2.6.1.4. 2.6.1.5. | Every chimney, flue and flue pipe shall be inspected and cleaned as often as necessary to keep them free from accumulations of combustible deposits. | Annually | Please select a designate. |
| Test | 2.6.1.8. | Disconnect switches for mechanical air-conditioning and ventilating systems shall be tested to establish that the system can be shut down in an emergency. | Annually | Please select a designate. |
|  | 2.6.3.3. | Spark arresters shall be cleaned annually or more frequently where accumulations of debris will adversely affect operations. Burnt-out arresters shall be repaired or replaced. | Annually or more frequently | Please select a designate. |

Water supplies for fire protection (water tanks)	   ☐ Check if this section is not applicable

*Additional reference to NFPA 25

| Check, inspect or test | Ontario Fire Code reference | Action | Frequency | Responsibility |
| --- | --- | --- | --- | --- |
|  | 6.6.1.1. | Private and public water supplies for fire protection installations shall be maintained to provide the required flow under fire conditions. | Annually | Contractor |
| Inspect | 6.6.1.2.(1) | Valves controlling water supplies used exclusively for fire protection systems or combined domestic water supplies and fire protection systems shall be sealed in the open position. | Weekly | Please select a designate. |
| Inspect | 6.6.1.2.(2) | Valves that are locked open or electrically supervised shall be inspected. | Monthly | Please select a designate. |
| Inspect | 6.6.1.2.(3) | After any alterations or repairs, an inspection shall be made to ensure valves are returned to the fully open position and are sealed, locked or electrically supervised. | As required | Please select a designate. |
|  | 6.6.1.3. | Water supply systems used for fire protection shall be kept free of ice accumulations that may interfere with flow. | As required | Please select a designate. |
| Check | 6.6.2.3. | A check of the temperature of the water contained in tanks shall be carried out during freezing weather to ensure that it does not fall below the freezing temperature. | Daily | Please select a designate. |
| Check | 6.6.2.4. | A check of the temperature of the tank enclosure for tanks in buildings shall be carried out during freezing weather to ensure that the temperature of the tank enclosure does not fall below 0°C. | Daily | Please select a designate. |
| Check | 6.6.2.12(1) | Pressure tanks shall be checked, and the water level shall be observed, and the air pressure shall be read. | Weekly | Please select a designate. |
| Inspect | 6.6.2.1. | An inspection shall be made of tanks for fire protection, tank supporting structures and water supply systems, including piping, control valves, check valves, heating systems, mercury gauges and expansion joints, to ensure that they are in operating condition. | Annually | Contractor |
| Check | 6.6.2.5. 6.6.2.6.(1) | Water tanks shall be checked inside and out for corrosion and sediment. | Every 2 years | Please select a designate. |
| Inspect | 6.6.2.6(2) | Tanks shall be inspected and scraped and repainted as required. | Every 5 years | Please select a designate. |
| Inspect | 6.6.2.7. | Cathodic protection equipment in water tanks shall be inspected. | Annually | Contractor |
| Inspect | 6.6.2.8 | Water level in gravity tanks shall be inspected. | Monthly | Please select a designate. |
| Inspect | 6.6.2.13 | Relief valves on the air and the water lines shall be inspected. | Weekly | Please select a designate. |

## Part 10	Additional information

Please enter any additional information, pertaining to your building, that has not already been covered in this document.

## Part 11	Building schematics

LEGEND FOR BUILDING / UNIT FIRE EMERGENCY SYSTEM

Please provide a schematic (floor plan) for each floor of your building. Hand drawings must be legible, otherwise computer programs are required. Include any of the following symbols to not the locations of these items.

FACP

M

The following are suggested:

Fire alarm control panel	Manuel pull station

FAA

F

Fire alarm annunciator					Fuel supply location

E

S

Main electrical shut off 	Smoke detector (stairwells/corridors)

W

N

H

Main water shut off	Heat detector (elevator shafts/ storage / service rooms)

Natural gas shut off valves

S

D

Sprinkler room shut off valves	Duct type smoke detector

FF

Standpipes							Firefighter elevator

N

Fire pump							North symbol

E

Portable fire extinguisher					Emergency light

K

EXIT

K-Class extinguisher						Exits

## Part 12	Site plan

A site plan of your property will include:

- Location of the property on the city street – including the street name.

- Location of cross streets (where applicable).

- Fire access route from street to building’s principal entrance (firefighters access point).

Include any of the following symbols to note the locations of these items.

N

H

Hydrants					          Natural gas

Designated gathering area			          Fire department connection

N

S

Approved smoking area			          North symbol

E

Electrical shut off

## Persons requiring assistance

Persons that require assistance in the event of an evacuation of the building are requested to advise management in order that they may render assistance. In some cases, you may not be able to leave, and you may have to stay and shelter in place. The list of persons requiring assistance is required to be updated as often as necessary by management. An updated list will be kept in the same location as the approved Fire Safety Plan within the building.

| Name | Location, room number, floor | Condition (optional) |
| --- | --- | --- |